## Price
Due to simplification of the optimization, initially one cable sizing will be chosen. However, in further development of the optimization, multiple cable sizing and prices need to be considered for each line before only one cable type and size is selected.
| Cross Section Area (mm^2) | Price |  | price (INR) | (SGD)
22 kV | 150 | 28.265 | SGD/m | 997 | 20.937 | Reference: http://www.havells.com/content/dam/havells/brouchers/Industrial%20Cable/Industrial%20Cable%20price%20list.pdf
| 185 | 33.453 | SGD/m | 1180 | 24.78
| 240 | 38.471 | SGD/m | 1357 | 28.497
| 300 | 43.3188 | SGD/m | 1528 | 32.088
| 400 | 51.2568 | SGD/m | 1808 | 37.968
| 500 | 63.2772 | SGD/m | 2232 | 46.872 |  | 35 % tax and fees are added to the netto customs declared price
| 630 | 75.0708 | SGD/m | 2648 | 55.608
| 800 | 87.6866 | SGD/m | 3093 | 64.953
| 1000 | 112.833 | SGD/m | 3980 | 83.58

## TechSpec22kV
|  |  | X = XL - Graigner |  | BC = 1 / XC - Graigner |  | XC = 1 / (ωC) | X = XL = ωL - Graigner
12.7/22 kV | Cable Cross Section | R | X | Z | Bsh | Smax | C | L | Y | G | B | Imax
Copper | mm2 | Ω/km | Ω/km | Ω/km | S/km | MVA | μF/km | mH/km | Ω/km | S/km | S/km | Amps
| 25 | R: 0.93; X = XL - Graigner Z: 0.93; X = XL = ωL - Graigner Y: 1.0753; X = XL = ωL - Graigner G: 1.0753; X = XL = ωL - Graigner B: 0
| 35 | R: 0.671; X = XL - Graigner Z: 0.671; X = XL = ωL - Graigner Y: 1.4903; X = XL = ωL - Graigner G: 1.4903; X = XL = ωL - Graigner B: 0
| 50 | 0.495 | 0.137 | 0.51361 |  |  |  | 0.43631 | 1.947 | 1.8765 | 0.51934
| 70 | 0.343 | 0.13 | 0.36681 |  |  |  | 0.41401 | 2.7262 | 2.5493 | 0.96619
| 95 | 0.247 | 0.124 | 0.27638 | 5.966e-05 | 10.0979 | 0.19 | 0.3949 | 3.6182 | 3.2336 | 1.6234 | 265
| 120 | 0.196 | 0.119 | 0.2293 | 6.28e-05 | 11.4315 | 0.2 | 0.37898 | 4.3612 | 3.7279 | 2.2633 | 300
| 150 | 0.159 | 0.115 | 0.19623 | 6.908e-05 | 12.5747 | 0.22 | 0.36624 | 5.0961 | 4.1292 | 2.9865 | 330
| 185 | 0.127 | 0.114 | 0.17066 | 7.536e-05 | 14.2894 | 0.24 | 0.36306 | 5.8596 | 4.3605 | 3.9142 | 375
| 240 | 0.0965 | 0.11 | 0.14633 | 8.164e-05 | 16.3852 | 0.26 | 0.35032 | 6.8339 | 4.5068 | 5.1372 | 430
| 300 | 0.0769 | 0.105 | 0.13015 | 9.42e-05 | 18.2905 | 0.3 | 0.33439 | 7.6835 | 4.5399 | 6.1989 | 480
| 400 | 0.0602 | 0.101 | 0.11758 | 0.00010362 | 20.5768 | 0.33 | 0.32166 | 8.5049 | 4.3544 | 7.3056 | 540
| 500 | 0.0468 | 0.099 | 0.1095 | 0.00011304 | 22.8631 | 0.36 | 0.31529 | 9.132 | 3.9028 | 8.256 | 600
| 630 | 0.0362 | 0.095 | 0.10166 | 0.0001256 | 25.1494 | 0.4 | 0.30255 | 9.8364 | 3.5025 | 9.1917 | 660
| 800 | 0.0283 | 0.092 | 0.096254 | 0.0001413 | 27.4357 | 0.45 | 0.29299 | 10.3891 | 3.0545 | 9.93 | 720
| 1000 | 0.0225 | 0.09 | 0.09277 | 0.00015386 | 28.9599 | 0.49 | 0.28662 | 10.7794 | 2.6144 | 10.4575 | 760
| Conductor Resistance (R) | X = XL = ωL - Graigner Y: Reference: http://www.prabhatcables.com/download/pdf-HT-XLPE.pdf
| Nominal Size of Conductor | R: Minimum no. of wires; X = XL - Graigner Z: Max. D.C. Resistance at 20° C; BC = 1 / XC - Graigner Smax: A.C. Resistance at 90° C
|  | Compacted Round |  | Plain Copper | Aluminium | Plain Copper | Aluminium
| Sq.mm | R: CU.; X = XL - Graigner X: ALU.; X = XL - Graigner Z: Ohm/Km; BC = 1 / XC - Graigner Bsh: Ohm/Km; BC = 1 / XC - Graigner Smax: Ohm/Km; XC = 1 / (ωC) C: Ohm/Km
| 25 | R: 6; X = XL - Graigner X: 6; X = XL - Graigner Z: 0.727; BC = 1 / XC - Graigner Bsh: 1.2; BC = 1 / XC - Graigner Smax: 0.93; XC = 1 / (ωC) C: 1.54
| 35 | R: 6; X = XL - Graigner X: 6; X = XL - Graigner Z: 0.524; BC = 1 / XC - Graigner Bsh: 0.868; BC = 1 / XC - Graigner Smax: 0.671; XC = 1 / (ωC) C: 1.11
| 50 | R: 6; X = XL - Graigner X: 6; X = XL - Graigner Z: 0.387; BC = 1 / XC - Graigner Bsh: 0.641; BC = 1 / XC - Graigner Smax: 0.495; XC = 1 / (ωC) C: 0.82
| 70 | R: 12; X = XL - Graigner X: 12; X = XL - Graigner Z: 0.268; BC = 1 / XC - Graigner Bsh: 0.443; BC = 1 / XC - Graigner Smax: 0.343; XC = 1 / (ωC) C: 0.567
| 95 | R: 15; X = XL - Graigner X: 15; X = XL - Graigner Z: 0.193; BC = 1 / XC - Graigner Bsh: 0.32; BC = 1 / XC - Graigner Smax: 0.247; XC = 1 / (ωC) C: 0.41
| 120 | R: 18; X = XL - Graigner X: 15; X = XL - Graigner Z: 0.153; BC = 1 / XC - Graigner Bsh: 0.253; BC = 1 / XC - Graigner Smax: 0.196; XC = 1 / (ωC) C: 0.324
| 150 | R: 18; X = XL - Graigner X: 15; X = XL - Graigner Z: 0.124; BC = 1 / XC - Graigner Bsh: 0.206; BC = 1 / XC - Graigner Smax: 0.159; XC = 1 / (ωC) C: 0.264
| 185 | R: 30; X = XL - Graigner X: 30; X = XL - Graigner Z: 0.0991; BC = 1 / XC - Graigner Bsh: 0.164; BC = 1 / XC - Graigner Smax: 0.127; XC = 1 / (ωC) C: 0.21
| 240 | R: 34; X = XL - Graigner X: 30; X = XL - Graigner Z: 0.0754; BC = 1 / XC - Graigner Bsh: 0.125; BC = 1 / XC - Graigner Smax: 0.0965; XC = 1 / (ωC) C: 0.16
| 300 | R: 34; X = XL - Graigner X: 30; X = XL - Graigner Z: 0.0601; BC = 1 / XC - Graigner Bsh: 0.1; BC = 1 / XC - Graigner Smax: 0.0769; XC = 1 / (ωC) C: 0.13
| 400 | R: 53; X = XL - Graigner X: 53; X = XL - Graigner Z: 0.047; BC = 1 / XC - Graigner Bsh: 0.0778; BC = 1 / XC - Graigner Smax: 0.0602; XC = 1 / (ωC) C: 0.1
| 500 | R: 53; X = XL - Graigner X: 53; X = XL - Graigner Z: 0.0366; BC = 1 / XC - Graigner Bsh: 0.0605; BC = 1 / XC - Graigner Smax: 0.0468; XC = 1 / (ωC) C: 0.0774
| 630 | R: 53; X = XL - Graigner X: 53; X = XL - Graigner Z: 0.0283; BC = 1 / XC - Graigner Bsh: 0.0469; BC = 1 / XC - Graigner Smax: 0.0362; XC = 1 / (ωC) C: 0.06
| 800 | R: 53; X = XL - Graigner X: 53; X = XL - Graigner Z: 0.0221; BC = 1 / XC - Graigner Bsh: 0.0367; BC = 1 / XC - Graigner Smax: 0.0283; XC = 1 / (ωC) C: 0.047
| 1000 | R: 53; X = XL - Graigner X: 53; X = XL - Graigner Z: 0.0176; BC = 1 / XC - Graigner Bsh: 0.0291; BC = 1 / XC - Graigner Smax: 0.0225; XC = 1 / (ωC) C: 0.0372
Short Circuit Rating for 1 sec duration (Ish) | bar: R to X = XL - Graigner X
| Nominal Size | R: XLPE Insulated
| Sq.mm | R: Copper; X = XL - Graigner X: Aluminium
| 25 | R: 3.6; X = XL - Graigner X: 2.4
| 35 | R: 5; X = XL - Graigner X: 3.3
| 50 | R: 7.1; X = XL - Graigner X: 4.7
| 70 | R: 10; X = XL - Graigner X: 6.6
| 95 | R: 13.6; X = XL - Graigner X: 9
| 120 | R: 17.1; X = XL - Graigner X: 11.3
| 150 | R: 21.4; X = XL - Graigner X: 14.2
| 185 | R: 26.4; X = XL - Graigner X: 17.5
| 240 | R: 34.3; X = XL - Graigner X: 22.6
| 300 | R: 42.9; X = XL - Graigner X: 28.3
| 400 | R: 57.1; X = XL - Graigner X: 37.7
| 500 | R: 71.4; X = XL - Graigner X: 47.2
| 630 | R: 90; X = XL - Graigner X: 59.4
| 800 | R: 114.3; X = XL - Graigner X: 75.5
| 1000 | R: 142.9; X = XL - Graigner X: 94.3
Approximate Capacitance for Single Core Cables (C) | bar: R to X = XL - Graigner Z
| Size | R: Voltage Grade (kV)
|  | 12.7/22 | 19/33 | 33/33
|  | μF/km | μF/km | μF/km
| 95 | R: 0.19; X = XL - Graigner X: 0.15; X = XL - Graigner Z: 0.14
| 120 | R: 0.2; X = XL - Graigner X: 0.16; X = XL - Graigner Z: 0.15
| 150 | R: 0.22; X = XL - Graigner X: 0.17; X = XL - Graigner Z: 0.16
| 185 | R: 0.24; X = XL - Graigner X: 0.18; X = XL - Graigner Z: 0.17
| 240 | R: 0.26; X = XL - Graigner X: 0.2; X = XL - Graigner Z: 0.19
| 300 | R: 0.3; X = XL - Graigner X: 0.23; X = XL - Graigner Z: 0.2
| 400 | R: 0.33; X = XL - Graigner X: 0.25; X = XL - Graigner Z: 0.23
| 500 | R: 0.36; X = XL - Graigner X: 0.27; X = XL - Graigner Z: 0.25
| 630 | R: 0.4; X = XL - Graigner X: 0.29; X = XL - Graigner Z: 0.28
| 800 | R: 0.45; X = XL - Graigner X: 0.33; X = XL - Graigner Z: 0.3
| 1000 | R: 0.49; X = XL - Graigner X: 0.35; X = XL - Graigner Z: 0.33
Approximate Reactance At 50 Hz For Single Core Cables (X) | bar: R to XC = 1 / (ωC) C
| Size | R: Voltage Grade(kV)
|  | 12.7/22 |  | 19/33 |  | 33/33
|  | Arm | Un-Arm | Arm | Un-Arm | Arm | Un-Arm
|  | Ohm/km | Ohm/km | Ohm/km | Ohm/km | Ohm/km | Ohm/km
| 50 | R: 0.137; X = XL - Graigner X: 0.13; X = XL - Graigner Z: 0.147; BC = 1 / XC - Graigner Bsh: 0.14
| 70 | R: 0.13; X = XL - Graigner X: 0.123; X = XL - Graigner Z: 0.141; BC = 1 / XC - Graigner Bsh: 0.133
| 95 | R: 0.124; X = XL - Graigner X: 0.116; X = XL - Graigner Z: 0.135; BC = 1 / XC - Graigner Bsh: 0.127; BC = 1 / XC - Graigner Smax: 0.143; XC = 1 / (ωC) C: 0.137
| 120 | R: 0.119; X = XL - Graigner X: 0.112; X = XL - Graigner Z: 0.13; BC = 1 / XC - Graigner Bsh: 0.122; BC = 1 / XC - Graigner Smax: 0.137; XC = 1 / (ωC) C: 0.131
| 150 | R: 0.115; X = XL - Graigner X: 0.107; X = XL - Graigner Z: 0.126; BC = 1 / XC - Graigner Bsh: 0.118; BC = 1 / XC - Graigner Smax: 0.134; XC = 1 / (ωC) C: 0.129
| 185 | R: 0.114; X = XL - Graigner X: 0.105; X = XL - Graigner Z: 0.124; BC = 1 / XC - Graigner Bsh: 0.115; BC = 1 / XC - Graigner Smax: 0.128; XC = 1 / (ωC) C: 0.122
| 240 | R: 0.11; X = XL - Graigner X: 0.101; X = XL - Graigner Z: 0.118; BC = 1 / XC - Graigner Bsh: 0.11; BC = 1 / XC - Graigner Smax: 0.124; XC = 1 / (ωC) C: 0.118
| 300 | R: 0.105; X = XL - Graigner X: 0.097; X = XL - Graigner Z: 0.112; BC = 1 / XC - Graigner Bsh: 0.105; BC = 1 / XC - Graigner Smax: 0.12; XC = 1 / (ωC) C: 0.114
| 400 | R: 0.101; X = XL - Graigner X: 0.093; X = XL - Graigner Z: 0.119; BC = 1 / XC - Graigner Bsh: 0.102; BC = 1 / XC - Graigner Smax: 0.115; XC = 1 / (ωC) C: 0.109
| 500 | R: 0.099; X = XL - Graigner X: 0.091; X = XL - Graigner Z: 0.105; BC = 1 / XC - Graigner Bsh: 0.099; BC = 1 / XC - Graigner Smax: 0.111; XC = 1 / (ωC) C: 0.106
| 630 | R: 0.095; X = XL - Graigner X: 0.089; X = XL - Graigner Z: 0.101; BC = 1 / XC - Graigner Bsh: 0.096; BC = 1 / XC - Graigner Smax: 0.108; XC = 1 / (ωC) C: 0.103
| 800 | R: 0.092; X = XL - Graigner X: 0.086; X = XL - Graigner Z: 0.097; BC = 1 / XC - Graigner Bsh: 0.092; BC = 1 / XC - Graigner Smax: 0.106; XC = 1 / (ωC) C: 0.099
| 1000 | R: 0.09; X = XL - Graigner X: 0.085; X = XL - Graigner Z: 0.096; BC = 1 / XC - Graigner Bsh: 0.09; BC = 1 / XC - Graigner Smax: 0.102; XC = 1 / (ωC) C: 0.096
“POLYCAB” SINGLE CORE COPPER CONDUCTOR, XLPE INSULATED, UNARMOURED & ARMOURED CABLES CONFORMING TO IS: 7098 PART-2/1985:
| Nominal Size of Conductor | R: Nominal Thickness of XLPE Insulation; X = XL - Graigner X: UNARMOURED CABLE; BC = 1 / XC - Graigner Smax: Min Thickness of Inner Sheath; XC = 1 / (ωC) C: ALUMINIUM STRIP ARMOURED CABLE; X = XL = ωL - Graigner B: ALUMINIUM ROUNDWIRE ARMOURED CABLE |  |  | CURRENT CARRYING CAPACITY |  |  | *Normal Delivery Length
|  |  | Nominal Thickness of PVC Outer Sheath | Approx. Overall Diameter of Cable | Approx. Weight of Cable |  | Nominal Dimesion of Strip | Minimum Thickness of PVC Outer Sheath | Approx. Overall Diameter of Cable | Approx. Weight of Cable | Nominal Dimesion of Round Wire | Minimum Thickness of PVC Outer Sheath | Approx. Overall Diameter of Cable | Approx. Weight of Cable | In Ground at 30° C. | In Duct at 30° C. | In Air at 40° C.
| Sq.mm. | mm | mm | mm | Kg/Km | mm | mm | mm | mm | Kg/Km | mm | mm | mm | Kg/Km | Amps. | Amps. | Amps. | Mtrs.
| 95 | 6 | 2.2 | 32 | 1650 | 0.4 | 0.8 | 1.56 | 33 | 1850 | 2 | 1.56 | 36 | 2050 | 265 | 230 | 345 | 500
| 120 | 6 | 2.2 | 34 | 1950 | 0.4 | 0.8 | 1.56 | 35 | 2150 | 2 | 1.56 | 37.5 | 2350 | 300 | 260 | 400 | 500
| 150 | 6 | 2.2 | 35 | 2250 | 0.4 | 0.8 | 1.56 | 36 | 2450 | 2 | 1.56 | 39 | 2700 | 330 | 290 | 450 | 500
| 185 | 6 | 2.2 | 37 | 2650 | 0.4 | 0.8 | 1.56 | 38 | 2850 | 2 | 1.72 | 41 | 3150 | 375 | 325 | 510 | 500
| 240 | 6 | 2.2 | 39 | 3200 | 0.4 | 0.8 | 1.56 | 40.5 | 3450 | 2 | 1.72 | 43 | 3750 | 430 | 370 | 600 | 500
| 300 | 6 | 2.2 | 41 | 3850 | 0.4 | 0.8 | 1.72 | 43 | 4100 | 2 | 1.72 | 45 | 4350 | 480 | 415 | 690 | 500
| 400 | 6 | 2.4 | 45 | 4900 | 0.5 | 0.8 | 1.88 | 47 | 5200 | 2 | 1.88 | 49 | 5500 | 540 | 465 | 790 | 500
| 500 | 6 | 2.6 | 48 | 5950 | 0.5 | 0.8 | 1.88 | 50 | 6200 | 2.5 | 2.04 | 53.5 | 6750 | 600 | 520 | 910 | 500
| 630 | 6 | 2.6 | 51.5 | 7200 | 0.5 | 0.8 | 2.04 | 54 | 7600 | 2.5 | 2.04 | 57 | 8050 | 660 | 570 | 1020 | 500
| 800 | 6 | 2.8 | 56 | 8950 | 0.6 | 0.8 | 2.04 | 58 | 9300 | 2.5 | 2.2 | 61 | 9900 | 720 | 620 | 1140 | 500
| 1000 | 6 | 3 | 61 | 11000 | 0.6 | 0.8 | 2.2 | 62.5 | 11350 | 2.5 | 2.36 | 66 | 12000 | 760 | 660 | 1240 | 500